## OldR
Media | t CO2 eq. | 2Ø / 1Ø | PFAS | Ref. Class | Psat @25°C (bar) | Vlimit | MW/m² | P_@calc(bar) | Pipe Diameter (mm) | Pipe Thickness (mm) | Pipe Tot. Cost (USD, 50m) | Normalized cost
INCOMP::MEG-25% | 0 | 1Ø | No | A1 | 0 | 2 | 78.9206 | 3 | 127.0164 | 0.26585 | 0.88923 | 1.0561
Water | 0 | 1Ø | No | A1 | 0.031699 | 2 | 83.3496 | 3 | 123.5957 | 0.25869 | 0.84198 | 1
CO2 | 1 | 2Ø | No | A1 | 64.3424 | 25 | 643.1234 | 64.3424 | 44.4947 | 3.3289 | 3.6164 | 4.2951
Ammonia | 1.37 | 2Ø | No | B2L | 10.0269 | 25 | 223.3663 | 10.0269 | 75.4999 | 0.88027 | 1.7334 | 2.0587
R290 | 0.02 | 2Ø | No | A3 | 9.5207 | 18 | 121.2451 | 9.5207 | 102.4762 | 1.1345 | 3.034 | 3.6034
Water | 0 | 2Ø | No | A1 | 0.031699 | 30 | 1.6677 | 3 | 873.7714 | 3.048 | 70.0374 | 83.1822
R1234ze(E) | 1.37 | 2Ø | Yes | A2L | 4.9852 | 20 | 86.048 | 4.9852 | 121.6423 | 0.70513 | 2.2504 | 2.6728
R1233zd(E) | 1 | 2Ø | No | B1 | 1.2981 | 20 | 27.1304 | 1.2981 | 216.634 | 0.32698 | 1.8665 | 2.2168
R152a | 124 | 2Ø | Yes | A2 | 5.9641 | 20 | 101.1197 | 5.9641 | 112.2114 | 0.77819 | 2.2884 | 2.7179
R32 | 675 | 2Ø | Yes | A2L | 16.8962 | 20 | 248.9802 | 16.8962 | 71.511 | 1.405 | 2.5992 | 3.0871
R134a | 1430 | 2Ø | Yes | A1 | 6.6538 | 20 | 112.4899 | 6.6538 | 106.3894 | 0.82313 | 2.2931 | 2.7235

## OldC
Component | Unit Price (EUR) | Quantity/Length | Total(EUR) | Cost (INCOMP::MEG-25%) | Cost (Water) | Cost (CO2) | Cost (Ammonia) | Cost (R290) | Cost (Water) | Cost (R1234ze(E)) | Cost (R1233zd(E)) | Cost (R152a) | Cost (R32) | Cost (R134a)
DN100 Pipe | 25 | 35 | 875 | 924.1052 | 875 | 3758.201 | 1801.3865 | 3152.9784 | 72784.3868 | 2338.6609 | 1939.6982 | 2378.1469 | 2701.1964 | 2383.0483
DN50 Hose | 5 | 64 | 320 | 337.9585 | 320 | 1374.4278 | 658.7928 | 1153.0893 | 26618.29 | 855.2817 | 709.3753 | 869.7223 | 987.8661 | 871.5148
T-Joints | 50 | 32 | 1600 | 1689.7924 | 1600 | 6872.139 | 3293.9639 | 5765.4463 | 133091.4502 | 4276.4084 | 3546.8767 | 4348.6114 | 4939.3306 | 4357.5741
Elbows DN100 | 12 | 4 | 48 | 50.6938 | 48 | 206.1642 | 98.8189 | 172.9634 | 3992.7435 | 128.2923 | 106.4063 | 130.4583 | 148.1799 | 130.7272
Main Isolation Valves DN100 | 500 | 8 | 4000 | 4224.481 | 4000 | 17180.3476 | 8234.9097 | 14413.6157 | 332728.6255 | 10691.0211 | 8867.1916 | 10871.5286 | 12348.3266 | 10893.9352
Rack Isolation Valves DN50 | 400 | 32 | 12800 | 13518.3393 | 12800 | 54977.1123 | 26351.7111 | 46123.5702 | 1064731.6016 | 34211.2675 | 28375.0132 | 34788.8914 | 39514.645 | 34860.5926
Weld Neck Flanges DN100 | 24 | 8 | 192 | 202.7751 | 192 | 824.6567 | 395.2757 | 691.8536 | 15970.974 | 513.169 | 425.6252 | 521.8334 | 592.7197 | 522.9089
Total |  |  | 19835 | 20948.1453 | 19835 | 85193.0486 | 40834.8585 | 71473.5169 | 1649918.0717 | 53014.1009 | 43970.1865 | 53909.1923 | 61232.2643 | 54020.3011
Item | Specification / Size | Quantity / Length | Unit Price (Approx.) | Subtotal (EUR) |  | # | Source | Description | Full URL
Pipe | DN 100, AISI 304, 35 meters | 35 meters | €25/m | 875 |  | 1 | Vijay Sales Corporation | Jindal SS 304 Pipes: Price List and Benefits | https://vijaysalescorp.com/jindal-ss304-pipes-price-list
Pipe or Hose | DN 50 to rack, 64 meters | 64 meters | €5/m | 320 |  | 2 | Integraflow | DN100 Schedule 40S Stainless Welded Pipe 304 | https://integraflow.co.uk/shop/ss-pip-100-sch40s
T-joints | T 100-50-100, AISI 304 | 32 pcs | 50 | 1600 |  | 3 | Alibaba | Dn100 Sch120 Od114mm Stainless Steel Pipe 304 | https://alibaba.com/showroom/dn100-sch120-od114mm-stainless-steel-pipe-304
Elbows (flanged) | DN 100, AISI 304 | 4 pcs | 12 | 48 |  | 4 | Swienty A/S | Hoses & Fittings | https://swientyfilling.com/pl/Accessories
Main Isolation Valves | DN 100 | 8 pcs | 500 | 4000 |  | 5 | Alibaba Mobile | Water hose pipe price list | https://m.alibaba.com/showroom/water-hose-pipe-price-list
Rack Isolation Valves | DN 50 | 32 pcs | 400 | 12800 |  | 6 | Alibaba | Aisi 304 Tee | https://alibaba.com/showroom/aisi-304-tee
Weld Neck Flanges | DN 100 | 8 pcs | 24 | 192 |  | 7 | Made-in-China (Yuzheng Valve) | DN100 Sanitary Stainless Steel Elbow | https://yuzhengvalve.en.made-in-china.com/product/BywxMRDn100-Stainless-Steel-Elbow.html
[6 empty] | 8 | Navstar Steel | Stainless Steel 304 Buttweld Fittings | https://navstarsteel.com/stainless-steel-304-buttweld-fittings
[6 empty] | 9 | Aesteiron | Stainless Steel 304 Pipe Fittings | https://aesteiron.com/stainless-steel-304-pipe-fittings
[6 empty] | 10 | NieRuf | Globe valve DN 100 Isolation plug | https://nieruf.com/Globe-valve-DN100-AV04-Isolation-plug
[6 empty] | 11 | Teka | Electro pneumatic isolating valves DN100 | https://teka.eu/en/Electro-pneumatic-isolating-valves-diam-100-mm
[6 empty] | 12 | NieRuf | Globe valve DN 50 Isolation plug | https://nieruf.com/Globe-valve-DN50-AV02-SG-iron-Isolation-plug
[6 empty] | 13 | Sale Engineering Products Ltd | SEP Priority Demand Valve – DN15-DN50 | https://firesprinkler.co.uk/product/sep-priority-demand-valve
[6 empty] | 14 | Pumpa Shop | Welding neck flange DN100 PN6 DIN 2631 | https://pumpa.eu/en/welding-neck-flange-dn100-pn6-din-2631
[6 empty] | 15 | Made-in-China (JS Pipe) | PE100 Pn16 50mm HDPE Pipe Price | https://jspipe.en.made-in-china.com/product/IXVxcsPE100-Pn16-50mm-HDPE-Pipe.html
[6 empty] | 16 | Ahlsell | T 100 Element for cover coupling | https://ahlsell.dk/en/produkter/t-100-element-cover-coupling
[6 empty] | 17 | END Shop | Weldneck flange neck DN100, PN16 | https://shop.end.de/en/fs000410
[6 empty] | 18 | HDPE Plumbing Trade | Trade List Price February 2024 | https://hdpeplumbingtrade.co.za/wp-content/uploads/TRADE-LIST-PRICE-FEBRUARY-2024.pdf
[6 empty] | 19 | Stainless Europe | Stainless steel seamless elbow DN100 | https://en.stainlesseurope.com/en_US/p/Stainless-steel-seamless-elbow-90-DN100
[6 empty] | 20 | END Shop | Ball valve DN100, PN16, full bore | https://shop.end.de/en/tf551010
[6 empty] | 21 | Scribd | Cost Estimation - Piping and Bulk material | https://scribd.com/document/80794765/Cost-Estimation-Piping-and-Bulk-material
[6 empty] | 22 | Made-in-China | SUS304 Stainless Steel Pipe Sch10 | https://made-in-china.com/price/prodetail/SUS304-Stainless-Steel-Pipe-Sch10.html
[6 empty] | 23 | Alibaba | 304 stainless steel pipe price kg | https://alibaba.com/showroom/304-stainless-steel-pipe-price-kg
[6 empty] | 24 | Alibaba | Sts304 stainless steel pipe price | https://alibaba.com/showroom/sts304-stainless-steel-pipe-price
[6 empty] | 25 | Alibaba | 304 stainless steel pipe price ton | https://alibaba.com/showroom/304-stainless-steel-pipe-price-ton
[6 empty] | 26 | Alibaba | 316L Stainless Steel Pipe Price Per Meter | https://alibaba.com/product-detail/316l-Stainless-Steel-Pipe-Price-Per-Meter-201.html
[6 empty] | 27 | Alibaba | 304 stainless steel pipe price | https://alibaba.com/showroom/304-stainless-steel-pipe-price
[6 empty] | 28 | Scribd | SS Pipe Price List (SS 316, SS 304) | https://scribd.com/document/451045678/SS-Pipe-Price-List-SS316-SS304.pdf

## RefCompCost0.55
Media | t CO2 eq. | 2Ø / 1Ø | PFAS | Ref. Class | Psat @25°C (bar) | Vlimit | MW/m² | P_@calc(bar) | Pipe Diameter (mm) | Pipe Thickness (mm) | Pipe Tot. Cost for *SS304* (USD, 1m) | Normalized cost
INCOMP::MEG-25% | 0 | 1Ø | No | A1 | 0 | 2 | 78.9206 | 3 | 127.0164 | 0.26585 | 0.88923 | 1.0561
Water | 0 | 1Ø | No | A1 | 0.031699 | 2 | 83.3496 | 3 | 123.5957 | 0.25869 | 0.84198 | 1
CO2 | 1 | 2Ø | No | A1 | 64.3424 | 25 | 557.1162 | 64.3424 | 47.806 | 3.5767 | 4.1747 | 4.9582
Ammonia | 1.37 | 2Ø | No | B2L | 10.0269 | 25 | 220.889 | 10.0269 | 75.9221 | 0.88519 | 1.7528 | 2.0818
R290 | 0.02 | 2Ø | No | A3 | 9.5207 | 18 | 118.2809 | 9.5207 | 103.7523 | 1.1486 | 3.11 | 3.6937
Water | 0 | 2Ø | No | A1 | 0.031699 | 30 | 1.6595 | 3 | 875.9311 | 3.0556 | 70.3841 | 83.5939
R1234ze(E) | 1.37 | 2Ø | Yes | A2L | 4.9852 | 20 | 84.7028 | 4.9852 | 122.6045 | 0.71071 | 2.2861 | 2.7152
R1233zd(E) | 1 | 2Ø | No | B1 | 1.2981 | 20 | 26.9228 | 1.2981 | 217.4679 | 0.32824 | 1.8809 | 2.2339
R152a | 124 | 2Ø | Yes | A2 | 5.9641 | 20 | 99.6376 | 5.9641 | 113.0429 | 0.78396 | 2.3224 | 2.7583
R32 | 675 | 2Ø | Yes | A2L | 16.8962 | 20 | 242.0687 | 16.8962 | 72.5247 | 1.4249 | 2.6735 | 3.1752
R134a | 1430 | 2Ø | Yes | A1 | 6.6538 | 20 | 110.5134 | 6.6538 | 107.3366 | 0.83046 | 2.3341 | 2.7722

## CompCost0.55
Component | Unit Price (EUR) | Quantity/Length | Total(EUR) | (INCOMP::MEG-25%) | (Water) | (CO2) | (Ammonia) | (R290) | (Water) | (R1234ze(E)) | (R1233zd(E)) | (R152a) | (R32) | (R134a)
DN100 Pipe | 25 | 35 | 875 | 924.1052 | 875 | 4338.3896 | 1821.5891 | 3231.9948 | 73144.6367 | 2375.8035 | 1954.6599 | 2413.5213 | 2778.3205 | 2425.6686
DN50 Hose | 5 | 64 | 320 | 337.9585 | 320 | 1586.6111 | 666.1811 | 1181.9867 | 26750.0386 | 868.8653 | 714.8471 | 882.6592 | 1016.0715 | 887.1016
T-Joints | 50 | 32 | 1600 | 1689.7924 | 1600 | 7933.0553 | 3330.9057 | 5909.9333 | 133750.1928 | 4344.3264 | 3574.2353 | 4413.2961 | 5080.3574 | 4435.5082
Elbows DN100 | 12 | 4 | 48 | 50.6938 | 48 | 237.9917 | 99.9272 | 177.298 | 4012.5058 | 130.3298 | 107.2271 | 132.3989 | 152.4107 | 133.0652
Main Isolation Valves DN100 | 500 | 8 | 4000 | 4224.481 | 4000 | 19832.6382 | 8327.2643 | 14774.8332 | 334375.4819 | 10860.816 | 8935.5883 | 11033.2402 | 12700.8936 | 11088.7706
Rack Isolation Valves DN50 | 400 | 32 | 12800 | 13518.3393 | 12800 | 63464.4421 | 26647.2458 | 47279.4662 | 1070001.5422 | 34754.6112 | 28593.8826 | 35306.3685 | 40642.8596 | 35484.0659
Weld Neck Flanges DN100 | 24 | 8 | 192 | 202.7751 | 192 | 951.9666 | 399.7087 | 709.192 | 16050.0231 | 521.3192 | 428.9082 | 529.5955 | 609.6429 | 532.261
Total based on *SS304* |  |  | 19835 | 33517.0324 | 31736 | 157352.1512 | 66068.515 | 117223.5265 | 2652935.0736 | 86169.7141 | 70894.9577 | 87537.7275 | 100768.89 | 87978.3059

## RefCompCost0.75
Media | t CO2 eq. | 2Ø / 1Ø | PFAS | Ref. Class | Psat @25°C (bar) | Vlimit | MW/m² | P_@calc(bar) | Pipe Diameter (mm) | Pipe Thickness (mm) | Pipe Tot. Cost (USD, 1m) | Normalized cost |  | DN external | Area
INCOMP::MEG-25% | 0 | 1Ø | No | A1 | 0 | 2 | 78.9206 | 3 | 127.0164 | 0.26585 | 0.88923 | 1.0561 | 106.2507 | DN125 | 0.012 | 0.94705
Water | 0 | 1Ø | No | A1 | 0.031699 | 2 | 83.3496 | 3 | 123.5957 | 0.25869 | 0.84198 | 1 | 100.6047
CO2 | 1 | 2Ø | No | A1 | 64.3424 | 25 | 643.1234 | 64.3424 | 44.4947 | 3.3289 | 3.6164 | 4.2951 | 499.8952 | DN50 | 0.002 | 1.2862
Ammonia | 1.37 | 2Ø | No | B2L | 10.0269 | 25 | 223.3663 | 10.0269 | 75.4999 | 0.88027 | 1.7334 | 2.0587
R290 | 0.02 | 2Ø | No | A3 | 9.5207 | 18 | 121.2451 | 9.5207 | 102.4762 | 1.1345 | 3.034 | 3.6034
Water | 0 | 2Ø | No | A1 | 0.031699 | 30 | 1.6677 | 3 | 873.7714 | 3.048 | 70.0374 | 83.1822
R1234ze(E) | 1.37 | 2Ø | Yes | A2L | 4.9852 | 20 | 86.048 | 4.9852 | 121.6423 | 0.70513 | 2.2504 | 2.6728
R1233zd(E) | 1 | 2Ø | No | B1 | 1.2981 | 20 | 27.1304 | 1.2981 | 216.634 | 0.32698 | 1.8665 | 2.2168
R152a | 124 | 2Ø | Yes | A2 | 5.9641 | 20 | 101.1197 | 5.9641 | 112.2114 | 0.77819 | 2.2884 | 2.7179
R32 | 675 | 2Ø | Yes | A2L | 16.8962 | 20 | 248.9802 | 16.8962 | 71.511 | 1.405 | 2.5992 | 3.0871
R134a | 1430 | 2Ø | Yes | A1 | 6.6538 | 20 | 112.4899 | 6.6538 | 106.3894 | 0.82313 | 2.2931 | 2.7235

## CompCost0.75
Component | Unit Price (EUR) | Quantity/Length | Total(EUR) | Cost (INCOMP::MEG-25%) | Cost (Water) | Cost (CO2) | Cost (Ammonia) | Cost (R290) | Cost (Water) | Cost (R1234ze(E)) | Cost (R1233zd(E)) | Cost (R152a) | Cost (R32) | Cost (R134a)
DN100 Pipe | 25 | 35 | 875 | 924.1052 | 875 | 3758.201 | 1801.3865 | 3152.9784 | 72784.3868 | 2338.6609 | 1939.6982 | 2378.1469 | 2701.1964 | 2383.0483
DN50 Hose | 5 | 64 | 320 | 337.9585 | 320 | 1374.4278 | 658.7928 | 1153.0893 | 26618.29 | 855.2817 | 709.3753 | 869.7223 | 987.8661 | 871.5148
T-Joints | 50 | 32 | 1600 | 1689.7924 | 1600 | 6872.139 | 3293.9639 | 5765.4463 | 133091.4502 | 4276.4084 | 3546.8767 | 4348.6114 | 4939.3306 | 4357.5741
Elbows DN100 | 12 | 4 | 48 | 50.6938 | 48 | 206.1642 | 98.8189 | 172.9634 | 3992.7435 | 128.2923 | 106.4063 | 130.4583 | 148.1799 | 130.7272
Main Isolation Valves DN100 | 500 | 8 | 4000 | 4224.481 | 4000 | 17180.3476 | 8234.9097 | 14413.6157 | 332728.6255 | 10691.0211 | 8867.1916 | 10871.5286 | 12348.3266 | 10893.9352
Rack Isolation Valves DN50 | 400 | 32 | 12800 | 13518.3393 | 12800 | 54977.1123 | 26351.7111 | 46123.5702 | 1064731.6016 | 34211.2675 | 28375.0132 | 34788.8914 | 39514.645 | 34860.5926
Weld Neck Flanges DN100 | 24 | 8 | 192 | 202.7751 | 192 | 824.6567 | 395.2757 | 691.8536 | 15970.974 | 513.169 | 425.6252 | 521.8334 | 592.7197 | 522.9089
Total |  |  | 19835 | 20948.1453 | 19835 | 85193.0486 | 40834.8585 | 71473.5169 | 1649918.0717 | 53014.1009 | 43970.1865 | 53909.1923 | 61232.2643 | 54020.3011

## RefCompCost0.95
Media | t CO2 eq. | 2Ø / 1Ø | PFAS | Ref. Class | Psat @25°C (bar) | Vlimit | MW/m² | P_@calc(bar) | Pipe Diameter (mm) | Pipe Thickness (mm) | Pipe Tot. Cost (USD, 50m) | Normalized cost
INCOMP::MEG-25% | 0 | 1Ø | No | A1 | 0 | 2 | 78.9206 | 3 | 127.0164 | 0.26585 | 0.88923 | 1.0561
Water | 0 | 1Ø | No | A1 | 0.031699 | 2 | 83.3496 | 3 | 123.5957 | 0.25869 | 0.84198 | 1
CO2 | 1 | 2Ø | No | A1 | 64.3424 | 25 | 705.71 | 64.3424 | 42.4758 | 3.1779 | 3.2956 | 3.9142
Ammonia | 1.37 | 2Ø | No | B2L | 10.0269 | 25 | 224.8147 | 10.0269 | 75.2563 | 0.87743 | 1.7222 | 2.0455
R290 | 0.02 | 2Ø | No | A3 | 9.5207 | 18 | 123.0161 | 9.5207 | 101.7358 | 1.1263 | 2.9903 | 3.5515
Water | 0 | 2Ø | No | A1 | 0.031699 | 30 | 1.6724 | 3 | 872.5283 | 3.0437 | 69.8383 | 82.9456
R1234ze(E) | 1.37 | 2Ø | Yes | A2L | 4.9852 | 20 | 86.8403 | 4.9852 | 121.0861 | 0.70191 | 2.2299 | 2.6484
R1233zd(E) | 1 | 2Ø | No | B1 | 1.2981 | 20 | 27.2512 | 1.2981 | 216.1535 | 0.32626 | 1.8582 | 2.207
R152a | 124 | 2Ø | Yes | A2 | 5.9641 | 20 | 101.9912 | 5.9641 | 111.731 | 0.77486 | 2.2688 | 2.6947
R32 | 675 | 2Ø | Yes | A2L | 16.8962 | 20 | 253.1321 | 16.8962 | 70.9221 | 1.3934 | 2.5566 | 3.0364
R134a | 1430 | 2Ø | Yes | A1 | 6.6538 | 20 | 113.6576 | 6.6538 | 105.8415 | 0.81889 | 2.2695 | 2.6955

## CompCost0.95
Component | Unit Price (EUR) | Quantity/Length | Total(EUR) | Cost (INCOMP::MEG-25%) | Cost (Water) | Cost (CO2) | Cost (Ammonia) | Cost (R290) | Cost (Water) | Cost (R1234ze(E)) | Cost (R1233zd(E)) | Cost (R152a) | Cost (R32) | Cost (R134a)
DN100 Pipe | 25 | 35 | 875 | 924.1052 | 875 | 3424.9012 | 1789.7808 | 3107.5861 | 72577.4348 | 2317.3236 | 1931.1031 | 2357.8254 | 2656.8911 | 2358.5644
DN50 Hose | 5 | 64 | 320 | 337.9585 | 320 | 1252.5353 | 654.5484 | 1136.4886 | 26542.6047 | 847.4783 | 706.232 | 862.2904 | 971.663 | 862.5607
T-Joints | 50 | 32 | 1600 | 1689.7924 | 1600 | 6262.6765 | 3272.742 | 5682.4431 | 132713.0236 | 4237.3917 | 3531.16 | 4311.4522 | 4858.3152 | 4312.8034
Elbows DN100 | 12 | 4 | 48 | 50.6938 | 48 | 187.8803 | 98.1823 | 170.4733 | 3981.3907 | 127.1218 | 105.9348 | 129.3436 | 145.7495 | 129.3841
Main Isolation Valves DN100 | 500 | 8 | 4000 | 4224.481 | 4000 | 15656.6913 | 8181.8549 | 14206.1078 | 331782.5591 | 10593.4793 | 8827.8999 | 10778.6304 | 12145.788 | 10782.0085
Rack Isolation Valves DN50 | 400 | 32 | 12800 | 13518.3393 | 12800 | 50101.4122 | 26181.9358 | 45459.5449 | 1061704.189 | 33899.1339 | 28249.2797 | 34491.6174 | 38866.5217 | 34502.4271
Weld Neck Flanges DN100 | 24 | 8 | 192 | 202.7751 | 192 | 751.5212 | 392.729 | 681.8932 | 15925.5628 | 508.487 | 423.7392 | 517.3743 | 582.9978 | 517.5364
Total |  |  | 19835 | 20948.1453 | 19835 | 77637.618 | 40571.7732 | 70444.537 | 1645226.7647 | 52530.4157 | 43775.3487 | 53448.5336 | 60227.9264 | 53465.2845